## Tasks Register
Task ID | Task Name | Equipment Group | Applies To (Instances) | Equipment Description | Task Type | Location | Department | Voltage | Lifting Equipment | Lifting Classification | Isolation Required | Task Scope / Activities | Weight (kg) | Job Description | Area, Equipment ID | Job Location | HP | Breaker Rating
REPLACE TASKS
T001 | REPLACE 460 VAC - 88FC MOTOR - COOLING WATER FAN MOTOR | 88FC | 88FC-1, 88FC-2, 88FC-3, 88FC-4, 88FC-5, 88FC-6 | COOLING WATER FAN MOTOR | REPLACE | Unit Cooling Water System Area | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift only (transport to/from Warehouse & Electrical Workshop + on-site handling) + Scaffold (Work at Height access) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); verify Scaffold is erected, inspected and tagged (green tag) before working at height; use full body harness with 100% tie-off; transport new motor from Warehouse to site by Forklift; disconnect electrical services; remove old motor and install new motor (lift/lower using Forklift); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; hand over Scaffold for dismantling; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Replace 460 VAC COOLING WATER FAN MOTOR (750 kg) in Unit Cooling Water System Area | • Area : Unit Cooling Water System Area • Equipment ID : 88FC - Cooling Water Fan Motor - 750 kg - 460 VAC, 3 PH, 60 Hz | UNIT COOLING WATER SYSTEM AREA | 30 | 70 A breaker
T004 | REPLACE 460 VAC - 88QV MOTOR - LUBE MIST SEPARATOR | 88QV | 88QV-1A | LUBE MIST SEPARATOR / ELIMINATOR MOTOR | REPLACE | Unit Enclosure | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (suspend and lift/lower motor on site) + Scaffold (Work at Height access) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); verify Scaffold is erected, inspected and tagged (green tag) before working at height; use full body harness with 100% tie-off; transport new motor from Warehouse to site by Forklift; disconnect electrical services; remove old motor and install new motor (lift/lower using Mobile Crane); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; hand over Scaffold for dismantling; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Replace 460 VAC LUBE MIST SEPARATOR / ELIMINATOR MOTOR (700 kg) in Unit Enclosure | • Area : Unit Enclosure • Equipment ID : 88QV - Lube Mist Separator / Eliminator Motor - 700 kg - 460 VAC, 3 PH, 60 Hz | UNIT ENCLOSURE | 10 | 20 A breaker
T007 | REPLACE 460 VAC - 88TK MOTOR - TURBINE EXHAUST FRAME COOLING BLOWER | 88TK | 88TK-1, 88TK-2 | TURBINE EXHAUST FRAME COOLING BLOWER | REPLACE | Unit Enclosure | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (suspend and lift/lower motor on site) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); transport new motor from Warehouse to site by Forklift; disconnect electrical services; open coupling (Electrical scope); remove old motor and install new motor (lift/lower using Mobile Crane); reconnect electrical services; perform rotation/function test; close coupling and complete alignment (Electrical scope); final inspection and housekeeping; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Replace 460 VAC TURBINE EXHAUST FRAME COOLING BLOWER (750 kg) in Unit Enclosure | • Area : Unit Enclosure • Equipment ID : 88TK - Turbine Exhaust Frame Cooling Blower - 750 kg - 460 VAC, 3 PH, 60 Hz | UNIT ENCLOSURE | 60 | 125 A breaker
T010 | REPLACE 460 VAC - 88WC MOTOR - COOLING WATER PUMP MOTOR | 88WC | 88WC-1, 88WC-2 | COOLING WATER PUMP MOTOR | REPLACE | Unit Cooling Water System Area | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift only (transport to/from Warehouse & Electrical Workshop + on-site handling) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); transport new motor from Warehouse to site by Forklift; disconnect electrical services; remove old motor and install new motor (lift/lower using Forklift); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 1500 kg | Replace 460 VAC COOLING WATER PUMP MOTOR (1500 kg) in Unit Cooling Water System Area | • Area : Unit Cooling Water System Area • Equipment ID : 88WC - Cooling Water Pump Motor - 1500 kg - 460 VAC, 3 PH, 60 Hz | UNIT COOLING WATER SYSTEM AREA | 125 | 250 A breaker
T016 | REPLACE 460 VAC - 88PF MOTOR - PRESSURIZING FAN MOTOR | 88PF | 88PF-1, 88PF-2 | PRESSURIZING FAN MOTOR | REPLACE | Above Accessory Compartment (Work at Height) | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (suspend and lift/lower motor on site) + Scaffold (Work at Height access) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); verify Scaffold is erected, inspected and tagged (green tag) before working at height; use full body harness with 100% tie-off; transport new motor from Warehouse to site by Forklift; disconnect electrical services; open coupling (Electrical scope); remove old motor and install new motor (lift/lower using Mobile Crane); reconnect electrical services; perform rotation/function test; close coupling and complete alignment (Electrical scope); final inspection and housekeeping; hand over Scaffold for dismantling; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 1500 kg | Replace 460 VAC PRESSURIZING FAN MOTOR (1500 kg) inside Above Accessory Compartment | • Area : Above Accessory Compartment • Equipment ID : 88PF - Pressurizing Fan Motor - 1500 kg - 460 VAC, 3 PH, 60 Hz | ABOVE ACCESSORY COMPARTMENT | 60 | 125 A breaker
T019 | REPLACE 460 VAC - 88AB MOTOR - ATOMIZING AIR COMPRESSOR MOTOR | 88AB | 88AB-1 | STARTING ATOMIZING AIR COMPRESSOR MOTOR | REPLACE | Accessory Compartment | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (external lift) + Chain Block (internal lift inside Accessory Compartment) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); transport new motor from Warehouse to site by Forklift; disconnect electrical services; remove old motor and install new motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Replace 460 VAC STARTING ATOMIZING AIR COMPRESSOR MOTOR (700 kg) inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88AB - Starting Atomizing Air Compressor Motor - 700 kg - 460 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 30 | 70 A breaker
T022 | REPLACE 480 VAC - 88HQ MOTOR - HYDRAULIC SUPPLY PUMP MOTOR | 88HQ | 88HQ-1 | HYDRAULIC SUPPLY PUMP MOTOR | REPLACE | Accessory Compartment | Electrical | 480 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (external lift) + Chain Block (internal lift inside Accessory Compartment) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); transport new motor from Warehouse to site by Forklift; disconnect electrical services; remove old motor and install new motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Replace 480 VAC HYDRAULIC SUPPLY PUMP MOTOR (700 kg) inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88HQ - Hydraulic Supply Pump Motor - 700 kg - 480 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 20 | 50 A breaker
T025 | REPLACE 460 VAC - 88QA MOTOR - AUXILIARY LUBE OIL PUMP MOTOR | 88QA | 88QA-1 | AUXILIARY LUBE OIL PUMP MOTOR | REPLACE | Accessory Compartment | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (external lift) + Chain Block (internal lift inside Accessory Compartment) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); transport new motor from Warehouse to site by Forklift; disconnect electrical services; remove old motor and install new motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 1500 kg | Replace 460 VAC AUXILIARY LUBE OIL PUMP MOTOR (1500 kg) inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88QA - Auxiliary Lube Oil Pump Motor - 1500 kg - 460 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 60 | 125 A breaker
T028 | REPLACE 460 VAC - 88TM MOTOR - TORQUE ADJUSTER DRIVE MOTOR | 88TM | 88TM-1 | TORQUE/SPEED ADJUSTER DRIVE MOTOR | REPLACE | Accessory Compartment | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (external lift) + Chain Block (internal lift inside Accessory Compartment) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); transport new motor from Warehouse to site by Forklift; disconnect electrical services; remove old motor and install new motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Replace 460 VAC TORQUE/SPEED ADJUSTER DRIVE MOTOR (700 kg) inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88TM - Torque/Speed Adjuster Drive Motor - 700 kg - 460 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 0.5 | 15 A breaker
T034 | REPLACE 125 VDC - 88QE MOTOR - EMERGENCY LUBE OIL PUMP MOTOR | 88QE | 88QE-1 | EMERGENCY LUBE OIL PUMP MOTOR | REPLACE | Accessory Compartment | Electrical | 125 VDC | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (external lift) + Chain Block (internal lift inside Accessory Compartment) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); transport new motor from Warehouse to site by Forklift; disconnect electrical services; remove old motor and install new motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Replace 125 VDC EMERGENCY LUBE OIL PUMP MOTOR (700 kg) inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88QE - Emergency Lube Oil Pump Motor - 700 kg - 125 VDC | ACCESSORY COMPARTMENT | 7.5 | Not found
T037 | REPLACE 480 VAC - CRUDE FWD MOTOR - CRUDE FWD MOTOR | CRUDE FWD | CRUDE FWD MOTOR | CRUDE FUEL FORWARDING PUMP MOTOR | REPLACE | Crude FWD Area | Electrical | 480 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Overhead Crane 5 Ton (fixed on platform — on-site lift/lower) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); transport new motor from Warehouse to site by Forklift; disconnect electrical services; remove old motor and install new motor (lift/lower using Overhead Crane 5 Ton); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Replace 480 VAC CRUDE FUEL FORWARDING PUMP MOTOR (750 kg) in Crude FWD Area | • Area : Crude FWD Area • Equipment ID : CRUDE FWD - Crude Fuel Forwarding Pump Motor - 750 kg - 480 VAC, 3 PH, 60 Hz | CRUDE FWD AREA | Not found | Not found
T040 | REPLACE 480 VAC - DIESEL FWD MOTOR - DIESEL FWD MOTOR | DIESEL FWD | DIESEL FWD MOTOR | DIESEL/DISTILLATE FUEL FORWARDING PUMP MOTOR | REPLACE | Diesel FWD Area | Electrical | 480 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Overhead Crane 5 Ton (fixed on platform — on-site lift/lower) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); transport new motor from Warehouse to site by Forklift; disconnect electrical services; remove old motor and install new motor (lift/lower using Overhead Crane 5 Ton); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; transport old motor to Electrical Workshop by Forklift; remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Replace 480 VAC DIESEL/DISTILLATE FUEL FORWARDING PUMP MOTOR (750 kg) in Diesel FWD Area | • Area : Diesel FWD Area • Equipment ID : DIESEL FWD - Diesel/Distillate Fuel Forwarding Pump Motor - 750 kg - 480 VAC, 3 PH, 60 Hz | DIESEL FWD AREA | Not found | Not found
MAINTAIN TASKS
T002 | MAINTAIN 460 VAC - 88FC MOTOR - COOLING WATER FAN MOTOR | 88FC | 88FC-1, 88FC-2, 88FC-3, 88FC-4, 88FC-5, 88FC-6 | COOLING WATER FAN MOTOR | MAINTAIN | Unit Cooling Water System Area | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift only (transport to/from Warehouse & Electrical Workshop + on-site handling) + Scaffold (Work at Height access) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); verify Scaffold is erected, inspected and tagged (green tag) before working at height; use full body harness with 100% tie-off; disconnect electrical services; remove motor (lift/lower using Forklift); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Forklift); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; hand over Scaffold for dismantling; remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Maintain 460 VAC COOLING WATER FAN MOTOR in Unit Cooling Water System Area | • Area : Unit Cooling Water System Area • Equipment ID : 88FC - Cooling Water Fan Motor - 750 kg - 460 VAC, 3 PH, 60 Hz | UNIT COOLING WATER SYSTEM AREA | 30 | 70 A breaker
T005 | MAINTAIN 460 VAC - 88QV MOTOR - LUBE MIST SEPARATOR | 88QV | 88QV-1A | LUBE MIST SEPARATOR / ELIMINATOR MOTOR | MAINTAIN | Unit Enclosure | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (suspend and lift/lower motor on site) + Scaffold (Work at Height access) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); verify Scaffold is erected, inspected and tagged (green tag) before working at height; use full body harness with 100% tie-off; disconnect electrical services; remove motor (lift/lower using Mobile Crane); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Mobile Crane); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; hand over Scaffold for dismantling; remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Maintain 460 VAC LUBE MIST SEPARATOR / ELIMINATOR MOTOR in Unit Enclosure | • Area : Unit Enclosure • Equipment ID : 88QV - Lube Mist Separator / Eliminator Motor - 700 kg - 460 VAC, 3 PH, 60 Hz | UNIT ENCLOSURE | 10 | 20 A breaker
T008 | MAINTAIN 460 VAC - 88TK MOTOR - TURBINE EXHAUST FRAME COOLING BLOWER | 88TK | 88TK-1, 88TK-2 | TURBINE EXHAUST FRAME COOLING BLOWER | MAINTAIN | Unit Enclosure | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (suspend and lift/lower motor on site) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); disconnect electrical services; open coupling (Electrical scope); remove motor (lift/lower using Mobile Crane); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Mobile Crane); reconnect electrical services; perform rotation/function test; close coupling and complete alignment (Electrical scope); final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Maintain 460 VAC TURBINE EXHAUST FRAME COOLING BLOWER in Unit Enclosure | • Area : Unit Enclosure • Equipment ID : 88TK - Turbine Exhaust Frame Cooling Blower - 750 kg - 460 VAC, 3 PH, 60 Hz | UNIT ENCLOSURE | 60 | 125 A breaker
T011 | MAINTAIN 460 VAC - 88WC MOTOR - COOLING WATER PUMP MOTOR | 88WC | 88WC-1, 88WC-2 | COOLING WATER PUMP MOTOR | MAINTAIN | Unit Cooling Water System Area | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift only (transport to/from Warehouse & Electrical Workshop + on-site handling) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); disconnect electrical services; remove motor (lift/lower using Forklift); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Forklift); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | 1500 kg | Maintain 460 VAC COOLING WATER PUMP MOTOR in Unit Cooling Water System Area | • Area : Unit Cooling Water System Area • Equipment ID : 88WC - Cooling Water Pump Motor - 1500 kg - 460 VAC, 3 PH, 60 Hz | UNIT COOLING WATER SYSTEM AREA | 125 | 250 A breaker
T014 | MAINTAIN 480 VAC - 88KA BREAKER - PEECC AIR CONDITIONER BREAKER (LOCAL CONTROL ROOM) | 88KA | 88KA-1, 88KA-2 | PEECC AIR CONDITIONER BREAKER (A/C unit maintained by A/C maintenance contractor — breaker maintenance only) | MAINTAIN | Local Control Room | Electrical | 480 VAC | N/A | N/A | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source on 88KA breaker (88KA-1 on MCC1-AC / 88KA-2 on MCC2-AC, Local Control Room) (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); breaker PM: general inspection, cleaning, terminal tightness check, mechanical operation check; final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | N/A | Maintain 480 VAC 88KA PEECC AIR CONDITIONER BREAKER inside Local Control Room | • Area : Local Control Room • Equipment ID : 88KA - PEECC Air Conditioner Breaker (MCC1-AC / MCC2-AC) - 480 VAC | LOCAL CONTROL ROOM | Not Provided | Not Provided
T017 | MAINTAIN 460 VAC - 88PF MOTOR - PRESSURIZING FAN MOTOR | 88PF | 88PF-1, 88PF-2 | PRESSURIZING FAN MOTOR | MAINTAIN | Above Accessory Compartment (Work at Height) | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (suspend and lift/lower motor on site) + Scaffold (Work at Height access) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); verify Scaffold is erected, inspected and tagged (green tag) before working at height; use full body harness with 100% tie-off; disconnect electrical services; open coupling (Electrical scope); remove motor (lift/lower using Mobile Crane); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Mobile Crane); reconnect electrical services; perform rotation/function test; close coupling and complete alignment (Electrical scope); final inspection and housekeeping; hand over Scaffold for dismantling; remove personal lock; return and close Work Permit at WCM Issuer Office. | 1500 kg | Maintain 460 VAC PRESSURIZING FAN MOTOR inside Above Accessory Compartment | • Area : Above Accessory Compartment • Equipment ID : 88PF - Pressurizing Fan Motor - 1500 kg - 460 VAC, 3 PH, 60 Hz | ABOVE ACCESSORY COMPARTMENT | 60 | 125 A breaker
T020 | MAINTAIN 460 VAC - 88AB MOTOR - ATOMIZING AIR COMPRESSOR MOTOR | 88AB | 88AB-1 | STARTING ATOMIZING AIR COMPRESSOR MOTOR | MAINTAIN | Accessory Compartment | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (external lift) + Chain Block (internal lift inside Accessory Compartment) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); disconnect electrical services; remove motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Maintain 460 VAC STARTING ATOMIZING AIR COMPRESSOR MOTOR inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88AB - Starting Atomizing Air Compressor Motor - 700 kg - 460 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 30 | 70 A breaker
T023 | MAINTAIN 480 VAC - 88HQ MOTOR - HYDRAULIC SUPPLY PUMP MOTOR | 88HQ | 88HQ-1 | HYDRAULIC SUPPLY PUMP MOTOR | MAINTAIN | Accessory Compartment | Electrical | 480 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (external lift) + Chain Block (internal lift inside Accessory Compartment) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); disconnect electrical services; remove motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Maintain 480 VAC HYDRAULIC SUPPLY PUMP MOTOR inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88HQ - Hydraulic Supply Pump Motor - 700 kg - 480 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 20 | 50 A breaker
T026 | MAINTAIN 460 VAC - 88QA MOTOR - AUXILIARY LUBE OIL PUMP MOTOR | 88QA | 88QA-1 | AUXILIARY LUBE OIL PUMP MOTOR | MAINTAIN | Accessory Compartment | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (external lift) + Chain Block (internal lift inside Accessory Compartment) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); disconnect electrical services; remove motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | 1500 kg | Maintain 460 VAC AUXILIARY LUBE OIL PUMP MOTOR inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88QA - Auxiliary Lube Oil Pump Motor - 1500 kg - 460 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 60 | 125 A breaker
T029 | MAINTAIN 460 VAC - 88TM MOTOR - TORQUE ADJUSTER DRIVE MOTOR | 88TM | 88TM-1 | TORQUE/SPEED ADJUSTER DRIVE MOTOR | MAINTAIN | Accessory Compartment | Electrical | 460 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (external lift) + Chain Block (internal lift inside Accessory Compartment) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); disconnect electrical services; remove motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Maintain 460 VAC TORQUE/SPEED ADJUSTER DRIVE MOTOR inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88TM - Torque/Speed Adjuster Drive Motor - 700 kg - 460 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 0.5 | 15 A breaker
T032 | MAINTAIN 480 VAC - 88HT BREAKER - HEATING AIR FAN BREAKER (LOCAL CONTROL ROOM) | 88HT | 88HT-4 | HEATING AIR FAN BREAKER (heater/fan not in service — breaker maintenance only) | MAINTAIN | Local Control Room | Electrical | 480 VAC | N/A | N/A | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source on 88HT breaker (MCC2-AC, Local Control Room) (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); breaker PM: general inspection, cleaning, terminal tightness check, mechanical operation check; final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | N/A | Maintain 480 VAC 88HT HEATING AIR FAN BREAKER inside Local Control Room | • Area : Local Control Room • Equipment ID : 88HT - Heating Air Fan Breaker (MCC2-AC) - 480 VAC | LOCAL CONTROL ROOM | Not Provided | Not Provided
T035 | MAINTAIN 125 VDC - 88QE MOTOR - EMERGENCY LUBE OIL PUMP MOTOR | 88QE | 88QE-1 | EMERGENCY LUBE OIL PUMP MOTOR | MAINTAIN | Accessory Compartment | Electrical | 125 VDC | Forklift (transport to/from Warehouse & Electrical Workshop) + Mobile Crane (external lift) + Chain Block (internal lift inside Accessory Compartment) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); disconnect electrical services; remove motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Mobile Crane (external) + Chain Block (internal lift inside Accessory Compartment)); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Maintain 125 VDC EMERGENCY LUBE OIL PUMP MOTOR inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88QE - Emergency Lube Oil Pump Motor - 700 kg - 125 VDC | ACCESSORY COMPARTMENT | 7.5 | Not found
T038 | MAINTAIN 480 VAC - CRUDE FWD MOTOR - CRUDE FWD MOTOR | CRUDE FWD | CRUDE FWD MOTOR | CRUDE FUEL FORWARDING PUMP MOTOR | MAINTAIN | Crude FWD Area | Electrical | 480 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Overhead Crane 5 Ton (fixed on platform — on-site lift/lower) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); disconnect electrical services; remove motor (lift/lower using Overhead Crane 5 Ton); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Overhead Crane 5 Ton); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Maintain 480 VAC CRUDE FUEL FORWARDING PUMP MOTOR in Crude FWD Area | • Area : Crude FWD Area • Equipment ID : CRUDE FWD - Crude Fuel Forwarding Pump Motor - 750 kg - 480 VAC, 3 PH, 60 Hz | CRUDE FWD AREA | Not found | Not found
T041 | MAINTAIN 480 VAC - DIESEL FWD MOTOR - DIESEL FWD MOTOR | DIESEL FWD | DIESEL FWD MOTOR | DIESEL/DISTILLATE FUEL FORWARDING PUMP MOTOR | MAINTAIN | Diesel FWD Area | Electrical | 480 VAC, 3 PH, 60 Hz | Forklift (transport to/from Warehouse & Electrical Workshop) + Overhead Crane 5 Ton (fixed on platform — on-site lift/lower) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver); disconnect electrical services; remove motor (lift/lower using Overhead Crane 5 Ton); transport motor to Electrical Workshop by Forklift; workshop PM: general inspection, cleaning, bearing replacement, fan replacement/check; transport motor back to site by Forklift; reinstall motor (lift/lower using Overhead Crane 5 Ton); reconnect electrical services; perform rotation/function test; final inspection and housekeeping; remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Maintain 480 VAC DIESEL/DISTILLATE FUEL FORWARDING PUMP MOTOR in Diesel FWD Area | • Area : Diesel FWD Area • Equipment ID : DIESEL FWD - Diesel/Distillate Fuel Forwarding Pump Motor - 750 kg - 480 VAC, 3 PH, 60 Hz | DIESEL FWD AREA | Not found | Not found
INSPECT TASKS
T003 | INSPECT 460 VAC - 88FC MOTOR - COOLING WATER FAN MOTOR | 88FC | 88FC-1, 88FC-2, 88FC-3, 88FC-4, 88FC-5, 88FC-6 | COOLING WATER FAN MOTOR | INSPECT | Unit Cooling Water System Area | Electrical | 460 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 460 VAC COOLING WATER FAN MOTOR in Unit Cooling Water System Area | • Area : Unit Cooling Water System Area • Equipment ID : 88FC - Cooling Water Fan Motor - 750 kg - 460 VAC, 3 PH, 60 Hz | UNIT COOLING WATER SYSTEM AREA | 30 | 70 A breaker
T006 | INSPECT 460 VAC - 88QV MOTOR - LUBE MIST SEPARATOR | 88QV | 88QV-1A | LUBE MIST SEPARATOR / ELIMINATOR MOTOR | INSPECT | Unit Enclosure | Electrical | 460 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 460 VAC LUBE MIST SEPARATOR / ELIMINATOR MOTOR in Unit Enclosure | • Area : Unit Enclosure • Equipment ID : 88QV - Lube Mist Separator / Eliminator Motor - 700 kg - 460 VAC, 3 PH, 60 Hz | UNIT ENCLOSURE | 10 | 20 A breaker
T009 | INSPECT 460 VAC - 88TK MOTOR - TURBINE EXHAUST FRAME COOLING BLOWER | 88TK | 88TK-1, 88TK-2 | TURBINE EXHAUST FRAME COOLING BLOWER | INSPECT | Unit Enclosure | Electrical | 460 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 460 VAC TURBINE EXHAUST FRAME COOLING BLOWER in Unit Enclosure | • Area : Unit Enclosure • Equipment ID : 88TK - Turbine Exhaust Frame Cooling Blower - 750 kg - 460 VAC, 3 PH, 60 Hz | UNIT ENCLOSURE | 60 | 125 A breaker
T012 | INSPECT 460 VAC - 88WC MOTOR - COOLING WATER PUMP MOTOR | 88WC | 88WC-1, 88WC-2 | COOLING WATER PUMP MOTOR | INSPECT | Unit Cooling Water System Area | Electrical | 460 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 460 VAC COOLING WATER PUMP MOTOR in Unit Cooling Water System Area | • Area : Unit Cooling Water System Area • Equipment ID : 88WC - Cooling Water Pump Motor - 1500 kg - 460 VAC, 3 PH, 60 Hz | UNIT COOLING WATER SYSTEM AREA | 125 | 250 A breaker
T018 | INSPECT 460 VAC - 88PF MOTOR - PRESSURIZING FAN MOTOR | 88PF | 88PF-1, 88PF-2 | PRESSURIZING FAN MOTOR | INSPECT | Above Accessory Compartment (Work at Height) | Electrical | 460 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 460 VAC PRESSURIZING FAN MOTOR inside Above Accessory Compartment | • Area : Above Accessory Compartment • Equipment ID : 88PF - Pressurizing Fan Motor - 1500 kg - 460 VAC, 3 PH, 60 Hz | ABOVE ACCESSORY COMPARTMENT | 60 | 125 A breaker
T021 | INSPECT 460 VAC - 88AB MOTOR - ATOMIZING AIR COMPRESSOR MOTOR | 88AB | 88AB-1 | STARTING ATOMIZING AIR COMPRESSOR MOTOR | INSPECT | Accessory Compartment | Electrical | 460 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 460 VAC STARTING ATOMIZING AIR COMPRESSOR MOTOR inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88AB - Starting Atomizing Air Compressor Motor - 700 kg - 460 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 30 | 70 A breaker
T024 | INSPECT 480 VAC - 88HQ MOTOR - HYDRAULIC SUPPLY PUMP MOTOR | 88HQ | 88HQ-1 | HYDRAULIC SUPPLY PUMP MOTOR | INSPECT | Accessory Compartment | Electrical | 480 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 480 VAC HYDRAULIC SUPPLY PUMP MOTOR inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88HQ - Hydraulic Supply Pump Motor - 700 kg - 480 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 20 | 50 A breaker
T027 | INSPECT 460 VAC - 88QA MOTOR - AUXILIARY LUBE OIL PUMP MOTOR | 88QA | 88QA-1 | AUXILIARY LUBE OIL PUMP MOTOR | INSPECT | Accessory Compartment | Electrical | 460 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 460 VAC AUXILIARY LUBE OIL PUMP MOTOR inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88QA - Auxiliary Lube Oil Pump Motor - 1500 kg - 460 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 60 | 125 A breaker
T030 | INSPECT 460 VAC - 88TM MOTOR - TORQUE ADJUSTER DRIVE MOTOR | 88TM | 88TM-1 | TORQUE/SPEED ADJUSTER DRIVE MOTOR | INSPECT | Accessory Compartment | Electrical | 460 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 460 VAC TORQUE/SPEED ADJUSTER DRIVE MOTOR inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88TM - Torque/Speed Adjuster Drive Motor - 700 kg - 460 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 0.5 | 15 A breaker
T036 | INSPECT 125 VDC - 88QE MOTOR - EMERGENCY LUBE OIL PUMP MOTOR | 88QE | 88QE-1 | EMERGENCY LUBE OIL PUMP MOTOR | INSPECT | Accessory Compartment | Electrical | 125 VDC | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 125 VDC EMERGENCY LUBE OIL PUMP MOTOR inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88QE - Emergency Lube Oil Pump Motor - 700 kg - 125 VDC | ACCESSORY COMPARTMENT | 7.5 | Not found
T039 | INSPECT 480 VAC - CRUDE FWD MOTOR - CRUDE FWD MOTOR | CRUDE FWD | CRUDE FWD MOTOR | CRUDE FUEL FORWARDING PUMP MOTOR | INSPECT | Crude FWD Area | Electrical | 480 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 480 VAC CRUDE FUEL FORWARDING PUMP MOTOR in Crude FWD Area | • Area : Crude FWD Area • Equipment ID : CRUDE FWD - Crude Fuel Forwarding Pump Motor - 750 kg - 480 VAC, 3 PH, 60 Hz | CRUDE FWD AREA | Not found | Not found
T042 | INSPECT 480 VAC - DIESEL FWD MOTOR - DIESEL FWD MOTOR | DIESEL FWD | DIESEL FWD MOTOR | DIESEL/DISTILLATE FUEL FORWARDING PUMP MOTOR | INSPECT | Diesel FWD Area | Electrical | 480 VAC, 3 PH, 60 Hz | N/A | N/A | No — Live inspection from authorized points, no isolation | PM inspection without isolation: sound check; vibration check; alignment check; voltage and current measurement from authorized/designated measurement points only; no isolation, LOTO or personal lock required for this task. | N/A | Inspect 480 VAC DIESEL/DISTILLATE FUEL FORWARDING PUMP MOTOR in Diesel FWD Area | • Area : Diesel FWD Area • Equipment ID : DIESEL FWD - Diesel/Distillate Fuel Forwarding Pump Motor - 750 kg - 480 VAC, 3 PH, 60 Hz | DIESEL FWD AREA | Not found | Not found
T043 | REPLACE BEARING OF 88WC MOTOR - COOLING WATER PUMP MOTOR | 88WC | 88WC-1, 88WC-2 | COOLING WATER PUMP MOTOR | REPLACE BEARING | Unit Cooling Water System Area | Electrical | 460 VAC, 3 PH, 60 Hz | None (no motor transport or lift required) | Routine (no lifting equipment involved) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver) (no disconnection of electrical cable terminals required); open motor front and rear end bells; remove old front and rear bearings; install new bearings and apply grease; reassemble motor end bells; final inspection and housekeeping (includes disposal of old bearings and hazardous waste — grease/CRC/WD40 if used); remove personal lock; return and close Work Permit at WCM Issuer Office. | 1500 kg | Replace bearing of 460 VAC COOLING WATER PUMP MOTOR (1500 kg) in Unit Cooling Water System Area | • Area : Unit Cooling Water System Area • Equipment ID : 88WC - Cooling Water Pump Motor - 1500 kg - 460 VAC, 3 PH, 60 Hz | UNIT COOLING WATER SYSTEM AREA | 125 | 250 A breaker
T044 | REPLACE BEARING OF 88TK MOTOR - TURBINE EXHAUST FRAME COOLING BLOWER | 88TK | 88TK-1, 88TK-2 | TURBINE EXHAUST FRAME COOLING BLOWER | REPLACE BEARING | Unit Enclosure | Electrical | 460 VAC, 3 PH, 60 Hz | Chain Block + Mobile Crane (chain block suspended from crane hook — lower motor to ground on site, then re-lift after bearing replacement) | Routine (weight known, ≤80% equipment capacity, standard rigging) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver) (no disconnection of electrical cable terminals required); disconnect motor mechanical coupling from TK fan; rig chain block to crane hook and lower motor to ground near work area; open motor front and rear end bells; remove old bearings, install new bearings and apply grease; reassemble motor end bells; lift motor back into position using chain block and crane hook; reconnect motor mechanical coupling to TK fan; final inspection and housekeeping (includes disposal of old bearings and hazardous waste — grease/CRC/WD40 if used); remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Replace bearing of 460 VAC TURBINE EXHAUST FRAME COOLING BLOWER (750 kg) in Unit Enclosure | • Area : Unit Enclosure • Equipment ID : 88TK - Turbine Exhaust Frame Cooling Blower - 750 kg - 460 VAC, 3 PH, 60 Hz | UNIT ENCLOSURE | 60 | 125 A breaker
T045 | REPLACE BEARING OF CRUDE FWD MOTOR - CRUDE FWD MOTOR | CRUDE FWD | CRUDE FWD MOTOR | CRUDE FUEL FORWARDING PUMP MOTOR | REPLACE BEARING | Crude FWD Area | Electrical | 480 VAC, 3 PH, 60 Hz | None (no motor transport or lift required) | Routine (no lifting equipment involved) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver) (no disconnection of electrical cable terminals required); open motor front and rear end bells; remove old front and rear bearings; install new bearings and apply grease; reassemble motor end bells; final inspection and housekeeping (includes disposal of old bearings and hazardous waste — grease/CRC/WD40 if used); remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Replace bearing of 480 VAC CRUDE FUEL FORWARDING PUMP MOTOR (750 kg) in Crude FWD Area | • Area : Crude FWD Area • Equipment ID : CRUDE FWD - Crude Fuel Forwarding Pump Motor - 750 kg - 480 VAC, 3 PH, 60 Hz | CRUDE FWD AREA | Not found | Not found
T046 | REPLACE BEARING OF DIESEL FWD MOTOR - DIESEL FWD MOTOR | DIESEL FWD | DIESEL FWD MOTOR | DIESEL/DISTILLATE FUEL FORWARDING PUMP MOTOR | REPLACE BEARING | Diesel FWD Area | Electrical | 480 VAC, 3 PH, 60 Hz | None (no motor transport or lift required) | Routine (no lifting equipment involved) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver) (no disconnection of electrical cable terminals required); open motor front and rear end bells; remove old front and rear bearings; install new bearings and apply grease; reassemble motor end bells; final inspection and housekeeping (includes disposal of old bearings and hazardous waste — grease/CRC/WD40 if used); remove personal lock; return and close Work Permit at WCM Issuer Office. | 750 kg | Replace bearing of 480 VAC DIESEL/DISTILLATE FUEL FORWARDING PUMP MOTOR (750 kg) in Diesel FWD Area | • Area : Diesel FWD Area • Equipment ID : DIESEL FWD - Diesel/Distillate Fuel Forwarding Pump Motor - 750 kg - 480 VAC, 3 PH, 60 Hz | DIESEL FWD AREA | Not found | Not found
T047 | REPLACE BEARING OF 88HQ MOTOR - HYDRAULIC SUPPLY PUMP MOTOR | 88HQ | 88HQ-1 | HYDRAULIC SUPPLY PUMP MOTOR | REPLACE BEARING | Accessory Compartment | Electrical | 480 VAC, 3 PH, 60 Hz | Chain Block only (internal support/lift inside Accessory Compartment — no motor removal, no Mobile Crane required) | Routine (no motor removal, no external lift) — JSA + TBT + Permit only | Yes — Electrical Isolation (LOTO) | Joint site walk-down with Permit Issuer and Permit Receiver (energy sources, SIMOPS, site conditions); verify equipment/tools certification and inspect PPE condition; process isolation request in system; isolate energy source (Permit Issuer); verify zero voltage / zero energy (Permit Issuer only); apply isolation lock/tag (Permit Issuer only); obtain Work Permit (PTW) (Permit Issuer + Permit Receiver); conduct Toolbox Talk and PPE Briefing (Permit Receiver); verify boundary tag and isolation lock are applied (Permit Receiver); apply Personal Lock (Permit Receiver) (no disconnection of electrical cable terminals required); rig chain block to motor lifting point; open motor front and rear end bells; support motor/rotor weight using chain block and remove old bearings; install new bearings and apply grease; release chain block and reassemble motor end bells; final inspection and housekeeping (includes disposal of old bearings and hazardous waste — grease/CRC/WD40 if used); remove personal lock; return and close Work Permit at WCM Issuer Office. | 700 kg | Replace bearing of 480 VAC HYDRAULIC SUPPLY PUMP MOTOR (700 kg) inside Accessory Compartment | • Area : Accessory Compartment • Equipment ID : 88HQ - Hydraulic Supply Pump Motor - 700 kg - 480 VAC, 3 PH, 60 Hz | ACCESSORY COMPARTMENT | 20 | 50 A breaker

## Equipment Master List
Device Nomenclature | Device Description | Department | Voltage | Location | Notes
MCC1-AC — 480V
88BQ-1 | Bearing Drain Enlargement Exhauster | Electrical | 480V | Accessory Compartment
88FC-1 | Cooling Water Fan Motor | Electrical | 480V | Cooling Water Area | Work at Height applies (Scaffold required)
88FC-3 | Cooling Water Fan Motor | Electrical | 480V | Cooling Water Area | Work at Height applies (Scaffold required)
88FC-5 | Cooling Water Fan Motor | Electrical | 480V | Cooling Water Area | Work at Height applies (Scaffold required)
88QV-1A | Lube Mist Separator | Electrical | 480V | Unit Enclosure | Work at Height applies (Scaffold required)
88TK-1 | Turbine Exhaust Frame Cooling Blower | Electrical | 480V | Unit Enclosure
88WC-1 | Cooling Water Pump Motor | Electrical | 480V | Cooling Water Area
88KA-1 | PEECC Air Conditioner | Electrical | 480V | Local Control Room | A/C unit is A/C maintenance contractor scope (not Electrical) — Electrical maintains the breaker only, in Local Control Room
88PF-1 | Pressurizing Fan Motor | Electrical | 480V | Above Accessory Compartment | Work at Height applies (Scaffold required)
MCC2-AC — 480V
88AB-1 | Atomizing Air Compressor Motor | Electrical | 480V | Accessory Compartment
88FC-2 | Cooling Water Fan Motor | Electrical | 480V | Cooling Water Area | Work at Height applies (Scaffold required)
88FC-4 | Cooling Water Fan Motor | Electrical | 480V | Cooling Water Area | Work at Height applies (Scaffold required)
88FC-6 | Cooling Water Fan Motor | Electrical | 480V | Cooling Water Area | Work at Height applies (Scaffold required)
88WC-2 | Cooling Water Pump Motor | Electrical | 480V | Cooling Water Area
88HQ-1 | Hydraulic Supply Pump Motor | Electrical | 480V | Accessory Compartment
88KA-2 | PEECC Air Conditioner | Electrical | 480V | Local Control Room | A/C unit is A/C maintenance contractor scope (not Electrical) — Electrical maintains the breaker only, in Local Control Room
88QA-1 | Auxiliary Lube Oil Pump | Electrical | 480V | Accessory Compartment
88TK-2 | Turbine Exhaust Frame Cooling Blower | Electrical | 480V | Unit Enclosure
88TM-1 | Torque Adjuster Drive Motor | Electrical | 480V | Accessory Compartment
88HT-4 | Heating Air Fan | Electrical | 480V | Accessory Compartment | Heater/fan not in service (hot area) — breaker maintenance only, in Local Control Room
88PF-2 | Pressurizing Fan Motor | Electrical | 480V | Above Accessory Compartment | Work at Height applies (Scaffold required)
DC MCC — 125V
88QE-1 | Emergency Lube Oil Pump Motor #1 | Electrical | 125V DC | Accessory Compartment | Only DC device in this group
Fuel Forwarding (FWD)
— | Crude FWD Motor | Electrical | 480V | Crude FWD Area
— | Crude FWD Local Power Panel | Electrical | 480V | Crude FWD Area
— | Crude FWD Pump | Mechanical | — | Crude FWD Area | Mechanical scope — pump only
— | Diesel FWD Motor | Electrical | 480V | Diesel FWD Area
— | Diesel FWD Local Power Panel | Electrical | 480V | Diesel FWD Area
— | Diesel FWD Pump | Mechanical | — | Diesel FWD Area | Mechanical scope — pump only
Fuel Heating
— | Crude Oil Heater transformer | Electrical | 13800V | Heater Area
— | Crude Oil Heater panel | Electrical | 480V | Heater Area
Breakers In Control room
— | All MCC1-AC / MCC2-AC breakers (incl. AC Panel Board #1, DC MCC-1 Panel Board) | Electrical | 480V / 125V (per parent MCC) | Local Control Room (on MCC1 / MCC2) | Correct Equipment Location for any breaker-operation / isolation JSA step, regardless of motor/pump field location
480V Switchgear
13800V Switchgear

## Tasks Notes & Assumptions
Scope:
Task Register consolidated by equipment GROUP/TYPE (e.g. 88FC MOTOR covers 88FC-1 through 88FC-6) rather than one task set per individual instance — one JSA covers all units of the same motor type. Individual equipment tags covered by each group are listed in the 'Applies To (Instances)' column.
Task types:
Each equipment group has 3 standard tasks: REPLACE (full replacement with isolation and lifting; new motor collected from Warehouse and old motor delivered to Electrical Workshop by Forklift), MAINTAIN (PM with isolation: motor removed, transported by Forklift to the Electrical Workshop for inspection, cleaning, bearing/fan replacement, then returned and reinstalled), INSPECT (PM without isolation: sound, vibration, alignment, voltage/current measurement from authorized points only).
Lifting equipment rule:
Forklift is used by Electrical for all transport to/from the Warehouse and Electrical Workshop. On-site lifting: 88FC and 88WC: Forklift only. CRUDE FWD / DIESEL FWD: Overhead Crane 5 Ton (fixed on platform). Accessory Compartment groups (88AB, 88HQ, 88QA, 88TM, 88QE): Mobile Crane (external) + Chain Block (internal lift). 88QV, 88TK, 88PF: Mobile Crane to suspend and lift/lower the motor. Coupling: Electrical opens/closes coupling and completes alignment only for 88TK and 88PF; for all other groups this is Mechanical scope and is not included in the Electrical task scope. Scaffold (Work at Height access) is required for REPLACE and MAINTAIN tasks of 88PF, 88FC and 88QV.
Excluded from this register:
Crude/Diesel FWD Pumps (Mechanical department scope), Crude Oil Heater (different failure modes — needs its own task definitions, not motor-type Replace/Maintain/Inspect), and Breakers/Switchgear — all MCC1-AC / MCC2-AC / DC MCC breakers require maintenance, but this is deferred to PHASE 2 (a separate breaker-maintenance task set will be added later); the only breaker tasks already included now are 88HT (T032) and 88KA (T014). 88HT (Heating Air Fan): heater/fan is not used (hot area) — REPLACE and INSPECT tasks removed; only MAINTAIN of its breaker in the Local Control Room is kept (T032). 88KA (PEECC Air Conditioner): the A/C unit belongs to the A/C maintenance contractor, not Electrical — REPLACE and INSPECT tasks removed; only MAINTAIN of its breaker in the Local Control Room is kept (T014).
Equipment code note:
88FD-1 / 88FD-2 (Customer Fuel Forwarding Pump, Type O in the source PDF) were not force-mapped to Crude/Diesel FWD Motor — kept as separate, unconfirmed pending user mapping.
Nameplate data update:
User-supplied nameplate data for 88WC, 88FC, 88PF, 88TK, 88QA, 88HQ updated Voltage (460 VAC, 3 PH, 60 Hz — except 88HQ at 480 VAC, 3 PH, 60 Hz), added HP and Breaker Rating columns, 88TK description confirmed by user as 'Turbine Exhaust Frame Cooling Blower'. 'Area, Equipment ID' field format updated to: Location ( Code - Description - Weight - Voltage[, PH, Hz] ). Groups without supplied nameplate data show HP/Breaker as 'Not Provided' and keep their previously confirmed voltage without PH/Hz (not invented).
Full nameplate data update (2026-09-23):
User supplied complete nameplate data (Weight/Voltage/HP/Ampere) for 12 of 14 groups. Descriptions corrected to match nameplate wording: CRUDE FWD -> 'Crude Fuel Forwarding Pump Motor', DIESEL FWD -> 'Diesel/Distillate Fuel Forwarding Pump Motor', 88QV -> 'Lube Mist Separator / Eliminator Motor', 88AB -> 'Starting Atomizing Air Compressor Motor', 88TM -> 'Torque/Speed Adjuster Drive Motor'. 88QE voltage confirmed by user as 125 VDC. CRUDE FWD/DIESEL FWD/88QE HP or Ampere marked 'Not found' per source — not invented. 88TM weight was 'Not found' in nameplate data — kept the previously user-confirmed 700 kg default.
Lifting Classification (Routine vs Non-Routine) added per ISMS standard: Routine = weight known from Name Plate, load ≤80% of lifting equipment rated capacity, standard/approved rigging point → requires JSA + TBT + Work Permit only (no formal Lifting Plan). All REPLACE tasks in this register are classified Routine based on documented weights and standard rigging.

## Equipment Notes & Rules
Source:
MCC1-AC / MCC2-AC / DC MCC load tables (MCC_1_2.pdf) + user-confirmed field locations and department assignments (chat, 2026-09-23).
Department split rule:
Electrical department covers motors, control panels, and breakers. Mechanical department covers pumps, oil, filters, fuel lines, and water lines associated with the same equipment.
Voltage rule:
MCC1-AC and MCC2-AC are confirmed 480V (MCC Bus Rating Summary). DC MCC is confirmed 125V.
Breaker location rule:
All breakers listed in the MCC1-AC/MCC2-AC PDF (including AC Panel Board #1 and DC MCC-1 Panel Board) are physically located in the Local Control Room, on MCC1 and MCC2 — this is the correct Equipment Location for any JSA step about breaker operation or electrical isolation, regardless of where the associated motor or pump sits in the plant.
Excluded:
88FD-1 and 88FD-2 (Customer Fuel Forwarding Pump, Type O) were not force-mapped to the Crude/Diesel FWD motor+pump pair described separately by the user — kept as distinct rows to avoid inventing an unconfirmed link.
Status:
TBC = To Be Confirmed. Update this row-by-row as the user provides each equipment's name, location, department, and voltage.